| DESCRIPTIVE Mechanic governor Mechanically welded chassis with antivibration suspension Main line circuit breaker Radiator for core temperature of 48/50°C max with mechanical fan Protective grille for fan and rotating parts (CE option) 9 dB(A) silencer supplied separately Charger DC starting battery with electrolyte 12 V charge alternator and starter Delivered with oil and coolant -30°C Manual for use and installation POWER DEFINITION PRP : Prime Power is available for an unlimited number of annual operating hours in variable load applications, in accordance with ISO 8528-1. ESP : The standby power rating is applicable for supplying emergency power in variable load applications in accordance with ISO 8528-1. Overload is not allowed. TERMS OF USE According to the standard, the nominal power assigned by the genset is given for 25°C Air Intlet Temperature, of a barometric pressure of 100 kPA (100 m A.S.L), and 30 % relative humidity. For particular conditions in your installation, refer to the derating table. ASSOCIATED UNCERTAINTY For the generating sets used indoor, where the acoustic pressure levels depends on the installation conditions, it is not possible to specify the ambient noise level in the exploitation and maintenance instructions . You will also find in our exploitation and maintenance instructions a warning concerning the air noise dangers and the need to implement appropriated preventive measures. | J130K Engine ref. 6068TF220 Alternator ref. KH01050T Performance class G2 GENERAL CHARACTERISTICS Frequency (Hz) 50 Hz Voltage (V) 400/230 Standard Control Panel APM303 Optional control panel APM403 Optional Control Panel M80 Optional control panel Terminal block POWER Voltage ESP PRP Standby Amps kWe kVA kWe kVA 415/240 106 132 96 120 184 400/230 106 132 96 120 191 380/220 106 132 96 120 201 200/115 106 132 96 120 381 240 TRI 106 132 96 120 318 230 TRI 106 132 96 120 331 220 TRI 106 132 96 120 346 DIMENSIONS COMPACT VERSION Length (mm) 2370 Width (mm) 1114 Height (mm) 1470 Dry weight (kg) 1498 Tank capacity (L) 340 DIMENSIONS SOUNDPROOFED VERSION Type soundproofing M226 Length (mm) 3508 Width (mm) 1200 Height (mm) 1830 Dry weight (kg) 2088 Tank capacity (L) 340 Acoustic pressure level @1m in dB(A) 50Hz (75% PRP) 75 Sound power level guaranteed (Lwa) 50Hz (75% PRP) 93 Acoustic pressure level @7m in dB(A) 50Hz (75% PRP) 64 |
| --- | --- |

| J130K ENGINE CHARACTERISTICS |
| --- |
| GENERAL ENGINE DATA Engine brand JOHN DEERE Engine ref. 6068TF220 Air inlet system Turbo Cylinders configuration L Number of cylinders 6 Displacement (L) 6,72 Charge Air coolant Bore (mm) x Stroke (mm) 106 x 127 Compression ratio 17 : 1 Speed (RPM) 1500 Pistons speed (m/s) 6,35 Maximum stand-by power at rated RPM (kW) 120 Frequency regulation, steady state (%) +/- 2.5% BMEP @ PRP 50 Hz (bar) 13 Governor type Mechanical COOLING SYSTEM Radiator & Engine capacity (L) 27,30 Fan power (kW) 3 Fan air flow w/o restriction (m3/s) 4,40 Available restriction on air flow (mm H2O) 20 Type of coolant Glycol-Ethylene EMISSIONS Emission PM (mg/Nm3) 5% O2 60 Emission CO (mg/Nm3) 5% O2 140 Emission HC+NOx (g/kWh) 0 Emission HC (g/kW.h) | EXHAUST Exhaust gas temperature @ ESP 50Hz (°C) 581 Exhaust gas flow @ ESP 50Hz (L/s) 318 Max. exhaust back pressure (mm H2O) 750 FUEL Consumption @ 100% load ESP (L/h) 29,50 Consumption @ 100% PRP load (L/h) 26,70 Consumption @ 75% PRP load (L/h) 20,20 Consumption @ 50% PRP load (L/h) 14 Maximum fuel pump flow (L/h) 108 OIL Oil system capacity including filters (L) 21,50 Min. oil pressure (bar) 1 Max. oil pressure (bar) 5 Oil consumption 100% ESP 50Hz (L/h) 0,03 Oil sump capacity (L) 20,60 HEAT BALANCE Heat rejection to exhaust (kW) 94 Radiated heat to ambiant (kW) 14 Heat rejection to coolant HT (kW) 65 AIR INTAKE Max. intake restriction (mm H2O) 625 Intake air flow (L/s) 135 |

| J130K ALTERNATOR CHARACTERISTICS |
| --- |
| GENERAL DATA Alternator ref. KH01050T Number of Phase Three phase Power factor (Cos Phi) 0,80 Altitude (m) 0 à 1000 Overspeed (rpm) 2250 Number of pole 4 Capacity for maintaining short circuit at 3 ln for 10 s No Insulation class H T° class (H/125°), continuous 40°C H / 125°K T° class (H/163°C), standby 27°C H / 163°K Total Harmonic Distortion in no-load DHT (%) <2 AVR Regulation Yes Total Harmonic Distortion, on linear load DHT (%) <5 Wave form : NEMA=TIF <50 Wave form : CEI=FHT <2 Number of bearing Single Bearing Coupling Direct Voltage regulation at established rating (+/- %) 0,50 Recovery time (Delta U = 20% transcient) (ms) 500 Indication of protection IP 23 Technology Brushless | OTHER DATA Continuous Nominal Rating 40°C (kVA) 125 Standby Rating 27°C (kVA) 138 Efficiencies 100% of load (%) 92,30 Air flow (m3/s) 0,25 Short circuit ratio (Kcc) 0,4460 Direct axis synchro reactance unsaturated (Xd) (%) 329 Quadra axis synchro reactance unsaturated (Xq) (%) 167 Open circuit time constant (T'do) (ms) 2154 Direct axis transcient reactance saturated (X'd) (%) 15,20 Short circuit transcient time constant (T'd) (ms) 100 Direct axis subtranscient reactance saturated (X''d) (%) 9,10 Subtranscient time constant (T"d) (ms) 10 Quadra axis subtranscient reactance saturated (X"q) (%) 18,60 Subtranscient time constant (T"q) (ms) 10 Zero sequence reactance unsaturated (Xo) (%) 0,60 Negative sequence reactance saturated (X2) (%) 13,89 Armature time constant (Ta) (ms) 15 No load excitation current (io) (A) 0,66 Full load excitation current (ic) (A) 2,47 Full load excitation voltage (uc) (V) 30,60 Engine start (Delta U = 20% perm. or 30% trans.) (kVA) 311,31 Transcient dip (4/4 load) - PF : 0,8 AR (%) 13 No load losses (W) 2387,09 Heat rejection (W) 8250,83 Unbalanced load acceptance ratio (%) 100 |
| DIMENSIONS |
| Dimensions soundproofed version Type soundproofing M226 Length (mm) 3508 Width (mm) 1200 Height (mm) 1830 Dry weight (kg) 2088 Tank capacity (L) 340 Acoustic pressure level @1m in dB(A) 50Hz (75% PRP) 75 Sound power level guaranteed (Lwa) 50Hz (75% PRP) 93 Acoustic pressure level @7m in dB(A) 50Hz (75% PRP) 64 Dimensions DW soundproofed version Type soundproofing M226 DW Length (mm) 3560 Width (mm) 1200 Height (mm) 2182 Dry weight (kg) 2588 Tank capacity (L) 868 Acoustic pressure level @1m in dB(A) 50Hz (75% PRP) 74 Sound power level guaranteed (Lwa) 50Hz (75% PRP) 93 Acoustic pressure level @7m in dB(A) 50Hz (75% PRP) 64 | Dimensions DW compact version Type soundproofing Length (mm) 3560 Width (mm) 1180 Height (mm) 1822 Dry weight (kg) 1908 Tank capacity (L) 868 Acoustic pressure level @1m in dB(A) 50Hz (75% PRP) Sound power level guaranteed (Lwa) 50Hz (75% PRP) Acoustic pressure level @7m in dB(A) 50Hz (75% PRP) Dimensions DW 48h soundproofed version Type soundproofing M226 DW48 Length (mm) 3560 Width (mm) 1200 Height (mm) 2364 %PdnetE_5% 2656 Tank capacity (L) 1630 Acoustic pressure level @1m in dB(A) 50Hz (75% PRP) 74 Sound power level guaranteed (Lwa) 50Hz (75% PRP) 93 Acoustic pressure level @7m in dB(A) 50Hz (75% PRP) 64 |

| J130K CONTROL PANEL |
| --- |
| APM303, comprehensive and simple The APM303 is a versatile unit which can be operated in manual or automatic mode. It offers the following features: Measurements: phase-to-neutral and phase-to-phase voltages, fuel level (In option : active power currents, effective power, power factors, Kw/h energy meter, oil pressure and coolant temperature levels) Supervision: Modbus RTU communication on RS485 Reports: (In option : 2 configurable reports) Safety features: Overspeed, oil pressure,coolant temperatures, minimum and maximum voltage, minimum and maximum frequency (Maximum active power P<66kVA) Traceability: Stack of 12 stored events For further information, please refer to the data sheet for the APM303. | APM403, basic generating set and power plant control The APM403 is a versatile control unit which allows operation in manual or automatic mode Measurements : voltage and current kW/kWh/kVA power meters Standard specifications: Voltmeter, Frequency meter. Optional : Battery ammeter. J1939 CAN ECU engine control Alarms and faults: Oil pressure, Coolant temperature, Overspeed, Start-up failure, alternator min/max, Emergency stop button. Engine parameters: Fuel level, hour counter, battery voltage. Optional (standard at 24V): Oil pressure, water temperature. Event log/ Management of the last 300 genset events. Mains and genset protection Clock management USB connections, USB Host and PC, Communications : RS485 INTERFACE ModBUS protocol /SNMP Optional : Ethernet, GPRS, remote control, 3G, 4G, Websupervisor, SMS, E-mails |

| M80, transfer of information The M80 is a dual-function control unit. It can be used as a basic terminal block for connecting a control box and as an instrument panel with a direct read facility, with displays giving a global view of your generating set's basic parameters. Offers the following functions: Engine parameters: tachometer, working hours counter, coolant temperature indicator, oil pressure indicator, emergency stop button, customer connection terminal block, CE. | Basic terminal block The control unit can be used as a basic terminal block for connecting a control box. Offers the following functions: emergency stop button, customer connection terminal block, CE. |
| --- | --- |