| DESCRIPTIVE Mechanic governor Mechanically welded chassis with antivibration suspension Main line circuit breaker Radiator for core temperature of 48/50°C max with mechanical fan Protective grille for fan and rotating parts (CE option) 9 dB(A) silencer supplied separately Charger DC starting battery with electrolyte 12 V charge alternator and starter Delivered with oil and coolant -30°C Manual for use and installation POWER DEFINITION PRP : Prime Power is available for an unlimited number of annual operating hours in variable load applications, in accordance with ISO 8528-1. ESP : The standby power rating is applicable for supplying emergency power in variable load applications in accordance with ISO 8528-1. Overload is not allowed. TERMS OF USE According to the standard, the nominal power assigned by the genset is given for 25°C Air Intlet Temperature, of a barometric pressure of 100 kPA (100 m A.S.L), and 30 % relative humidity. For particular conditions in your installation, refer to the derating table. ASSOCIATED UNCERTAINTY For the generating sets used indoor, where the acoustic pressure levels depends on the installation conditions, it is not possible to specify the ambient noise level in the exploitation and maintenance instructions . You will also find in our exploitation and maintenance instructions a warning concerning the air noise dangers and the need to implement appropriated preventive measures. | J22 Engine ref. 3029DSG20 Alternator ref. KH00404T Performance class G3 GENERAL CHARACTERISTICS Frequency (Hz) 50 Hz Voltage (V) 400/230 Standard Control Panel APM303 Optional control panel APM403 POWER Voltage ESP PRP Standby Amps kWe kVA kWe kVA 415/240 17,6 22 16 20 31 400/230 17,6 22 16 20 32 380/220 17,6 22 16 20 33 DIMENSIONS COMPACT VERSION Length (mm) 1700 Width (mm) 896 Height (mm) 1181 Dry weight (kg) 624 Tank capacity (L) 100 DIMENSIONS SOUNDPROOFED VERSION Type soundproofing M137 Length (mm) 2100 Width (mm) 938 Height (mm) 1285 Dry weight (kg) 812 Tank capacity (L) 100 Acoustic pressure level @1m in dB(A) 50Hz (75% PRP) 75 Sound power level guaranteed (Lwa) 50Hz (75% PRP) 92 Acoustic pressure level @7m in dB(A) 50Hz (75% PRP) 63 |
| --- | --- |

| J22 ENGINE CHARACTERISTICS |
| --- |
| GENERAL ENGINE DATA Engine brand JOHN DEERE Engine ref. 3029DSG20 Air inlet system Athmo Cylinders configuration L Number of cylinders 3 Displacement (L) 2,91 Charge Air coolant Bore (mm) x Stroke (mm) 106 x 110 Compression ratio 17.2 : 1 Speed (RPM) 1500 Pistons speed (m/s) 5,50 Maximum stand-by power at rated RPM (kW) 31 Frequency regulation, steady state (%) +/- 2.5% BMEP @ PRP 50 Hz (bar) 7,70 Governor type Mechanical COOLING SYSTEM Radiator & Engine capacity (L) 16,10 Fan power (kW) 0,70 Fan air flow w/o restriction (m3/s) 1,74 Available restriction on air flow (mm H2O) 20 Type of coolant Glycol-Ethylene EMISSIONS Emission PM (mg/Nm3) 5% O2 74 Emission CO (mg/Nm3) 5% O2 1165 Emission HC+NOx (g/kWh) 17,40 Emission HC (g/kW.h) 1 | EXHAUST Exhaust gas temperature @ ESP 50Hz (°C) 555 Exhaust gas flow @ ESP 50Hz (L/s) 78 Max. exhaust back pressure (mm H2O) 625 FUEL Consumption @ 100% load ESP (L/h) 8,50 Consumption @ 100% PRP load (L/h) 7 Consumption @ 75% PRP load (L/h) 5 Consumption @ 50% PRP load (L/h) 3,60 Maximum fuel pump flow (L/h) 111 OIL Oil system capacity including filters (L) 6 Min. oil pressure (bar) 1 Max. oil pressure (bar) 5 Oil consumption 100% ESP 50Hz (L/h) 0,07 Oil sump capacity (L) 5,30 HEAT BALANCE Heat rejection to exhaust (kW) 31 Radiated heat to ambiant (kW) 6 Heat rejection to coolant HT (kW) 18 AIR INTAKE Max. intake restriction (mm H2O) 300 Intake air flow (L/s) 28 |

| J22 ALTERNATOR CHARACTERISTICS |
| --- |
| GENERAL DATA Alternator ref. KH00404T Number of Phase Three phase Power factor (Cos Phi) 0,80 Altitude (m) 0 à 1000 Overspeed (rpm) 2250 Number of pole 4 Capacity for maintaining short circuit at 3 ln for 10 s Yes Insulation class H T° class (H/125°), continuous 40°C H / 125°K T° class (H/163°C), standby 27°C H / 163°K Total Harmonic Distortion in no-load DHT (%) 3,6 AVR Regulation Yes Total Harmonic Distortion, on linear load DHT (%) 2,0 Wave form : NEMA=TIF <45 Wave form : CEI=FHT <2 Number of bearing Single Bearing Coupling Direct Voltage regulation at established rating (+/- %) 1 Recovery time (Delta U = 20% transcient) (ms) 200 Indication of protection IP 23 Technology Brushless | OTHER DATA Continuous Nominal Rating 40°C (kVA) 20 Standby Rating 27°C (kVA) 21,50 Efficiencies 100% of load (%) 87,40 Air flow (m3/s) 0,0880 Short circuit ratio (Kcc) 0,64 Direct axis synchro reactance unsaturated (Xd) (%) 184,50 Quadra axis synchro reactance unsaturated (Xq) (%) 80 Open circuit time constant (T'do) (ms) 850 Direct axis transcient reactance saturated (X'd) (%) 14,60 Short circuit transcient time constant (T'd) (ms) 44 Direct axis subtranscient reactance saturated (X''d) (%) 8,40 Subtranscient time constant (T"d) (ms) 14 Quadra axis subtranscient reactance saturated (X"q) (%) 19,20 Subtranscient time constant (T"q) (ms) 10 Zero sequence reactance unsaturated (Xo) (%) 3,38 Negative sequence reactance saturated (X2) (%) 12,50 Armature time constant (Ta) (ms) 12 No load excitation current (io) (A) 0,50 Full load excitation current (ic) (A) 1,50 Full load excitation voltage (uc) (V) 15,90 Engine start (Delta U = 20% perm. or 30% trans.) (kVA) 50,20 Transcient dip (4/4 load) - PF : 0,8 AR (%) 14,10 No load losses (W) 550 Heat rejection (W) 2307 Unbalanced load acceptance ratio (%) 100 |
| DIMENSIONS |
| Dimensions soundproofed version Type soundproofing M137 Length (mm) 2100 Width (mm) 938 Height (mm) 1285 Dry weight (kg) 812 Tank capacity (L) 100 Acoustic pressure level @1m in dB(A) 50Hz (75% PRP) 75 Sound power level guaranteed (Lwa) 50Hz (75% PRP) 92 Acoustic pressure level @7m in dB(A) 50Hz (75% PRP) 63 Dimensions DW soundproofed version Type soundproofing M137-DW Length (mm) 2100 Width (mm) 938 Height (mm) 1486 Dry weight (kg) 1120 Tank capacity (L) 240 Acoustic pressure level @1m in dB(A) 50Hz (75% PRP) 75 Sound power level guaranteed (Lwa) 50Hz (75% PRP) 92 Acoustic pressure level @7m in dB(A) 50Hz (75% PRP) 62 | Dimensions DW compact version Type soundproofing Length (mm) 2074 Width (mm) 932 Height (mm) 1382 Dry weight (kg) 832 Tank capacity (L) 240 Acoustic pressure level @1m in dB(A) 50Hz (75% PRP) Sound power level guaranteed (Lwa) 50Hz (75% PRP) Acoustic pressure level @7m in dB(A) 50Hz (75% PRP) Dimensions DW 48h soundproofed version Type soundproofing M137-DW48 Length (mm) 2100 Width (mm) 938 Height (mm) 1540 %PdnetE_5% 1032 Tank capacity (L) 470 Acoustic pressure level @1m in dB(A) 50Hz (75% PRP) 75 Sound power level guaranteed (Lwa) 50Hz (75% PRP) 92 Acoustic pressure level @7m in dB(A) 50Hz (75% PRP) 62 |

| J22 CONTROL PANEL |
| --- |
| APM303, comprehensive and simple The APM303 is a versatile unit which can be operated in manual or automatic mode. It offers the following features: Measurements: phase-to-neutral and phase-to-phase voltages, fuel level (In option : active power currents, effective power, power factors, Kw/h energy meter, oil pressure and coolant temperature levels) Supervision: Modbus RTU communication on RS485 Reports: (In option : 2 configurable reports) Safety features: Overspeed, oil pressure,coolant temperatures, minimum and maximum voltage, minimum and maximum frequency (Maximum active power P<66kVA) Traceability: Stack of 12 stored events For further information, please refer to the data sheet for the APM303. | APM403, basic generating set and power plant control The APM403 is a versatile control unit which allows operation in manual or automatic mode Measurements : voltage and current kW/kWh/kVA power meters Standard specifications: Voltmeter, Frequency meter. Optional : Battery ammeter. J1939 CAN ECU engine control Alarms and faults: Oil pressure, Coolant temperature, Overspeed, Start-up failure, alternator min/max, Emergency stop button. Engine parameters: Fuel level, hour counter, battery voltage. Optional (standard at 24V): Oil pressure, water temperature. Event log/ Management of the last 300 genset events. Mains and genset protection Clock management USB connections, USB Host and PC, Communications : RS485 INTERFACE ModBUS protocol /SNMP Optional : Ethernet, GPRS, remote control, 3G, 4G, Websupervisor, SMS, E-mails |