| DESCRIPTIVE Electronic governor Mechanically welded chassis with antivibration suspension Main line circuit breaker Radiator for core temperature of 48/50°C max with mechanical fan Protective grille for fan and rotating parts (CE option) 9 dB(A) silencer supplied separately Charger DC starting battery with electrolyte 24 V charge alternator and starter Delivered with oil and coolant -30°C Manual for use and installation POWER DEFINITION PRP : Prime Power is available for an unlimited number of annual operating hours in variable load applications, in accordance with ISO 8528-1. ESP : The standby power rating is applicable for supplying emergency power in variable load applications in accordance with ISO 8528-1. Overload is not allowed. TERMS OF USE According to the standard, the nominal power assigned by the genset is given for 25°C Air Intlet Temperature, of a barometric pressure of 100 kPA (100 m A.S.L), and 30 % relative humidity. For particular conditions in your installation, refer to the derating table. ASSOCIATED UNCERTAINTY For the generating sets used indoor, where the acoustic pressure levels depends on the installation conditions, it is not possible to specify the ambient noise level in the exploitation and maintenance instructions . You will also find in our exploitation and maintenance instructions a warning concerning the air noise dangers and the need to implement appropriated preventive measures. | V350C2 Engine ref. TAD1341GE Alternator ref. KH02100T Performance class G3 GENERAL CHARACTERISTICS Frequency (Hz) 50 Hz Voltage (V) 400/230 Standard Control Panel APM403 Optional control panel APM802 Optional Control Panel M80 Optional control panel Terminal block POWER Voltage ESP PRP Standby Amps kWe kVA kWe kVA 415/240 280 350 254 318 487 400/230 280 350 254 318 505 380/220 280 350 254 318 532 200/115 280 350 254 318 1010 240 TRI 280 350 254 318 842 230 TRI 280 350 254 318 879 220 TRI 280 350 254 318 919 DIMENSIONS COMPACT VERSION Length (mm) 3160 Width (mm) 1340 Height (mm) 1805 Dry weight (kg) 3103 Tank capacity (L) 470 DIMENSIONS AND NOISE LEVELS In compliance with 2000/14/CE standard Type soundproofing M228 Length (mm) 4475 Width (mm) 1410 Height (mm) 2430 Dry weight (kg) 4035 Tank capacity (L) 470 Acoustic pressure level @1m in dB(A) 50Hz (75% PRP) 77 Sound power level guaranteed (Lwa) 50Hz (75% PRP) 97 Acoustic pressure level @7m in dB(A) 50Hz (75% PRP) 67 |
| --- | --- |

| V350C2 ENGINE CHARACTERISTICS |
| --- |
| GENERAL ENGINE DATA Engine brand VOLVO Engine ref. TAD1341GE Air inlet system Turbo Cylinders configuration L Number of cylinders 6 Displacement (L) 12,78 Charge Air coolant Air/Air Bore (mm) x Stroke (mm) 131 x 158 Compression ratio 18.1 : 1 Speed (RPM) 1500 Pistons speed (m/s) 7,90 Maximum stand-by power at rated RPM (kW) 308 Frequency regulation, steady state (%) +/- 0.25% BMEP @ PRP 50 Hz (bar) 17,50 Governor type Electronic COOLING SYSTEM Radiator & Engine capacity (L) 44 Fan power (kW) 10 Fan air flow w/o restriction (m3/s) 7,50 Available restriction on air flow (mm H2O) 20 Type of coolant Glycol-Ethylene EMISSIONS Emission PM (g/kW.h) 0,08 Emission CO (g/kW.h) 0,56 Emission NOx (g/kW.h) 5,62 Emission HC (g/kW.h) 0,22 | EXHAUST Exhaust gas temperature @ ESP 50Hz (°C) 414 Exhaust gas flow @ ESP 50Hz (L/s) 867 Max. exhaust back pressure (mm H2O) 1000 FUEL Consumption @ 100% load ESP (L/h) 69,20 Consumption @ 100% PRP load (L/h) 62,90 Consumption @ 75% PRP load (L/h) 48,20 Consumption @ 50% PRP load (L/h) 33,30 Maximum fuel pump flow (L/h) 120 OIL Oil system capacity including filters (L) 36 Min. oil pressure (bar) Max. oil pressure (bar) Oil consumption 100% ESP 50Hz (L/h) 0,04 Oil sump capacity (L) 30 HEAT BALANCE Heat rejection to exhaust (kW) 203 Radiated heat to ambiant (kW) 10 Heat rejection to coolant HT (kW) 133 AIR INTAKE Max. intake restriction (mm H2O) 510 Intake air flow (L/s) 401 |

| V350C2 ALTERNATOR CHARACTERISTICS |
| --- |
| GENERAL DATA Alternator ref. KH02100T Number of Phase Three phase Power factor (Cos Phi) 0,80 Altitude (m) 0 à 1000 Overspeed (rpm) 2250 Number of pole 4 Capacity for maintaining short circuit at 3 ln for 10 s No Insulation class H T° class (H/125°), continuous 40°C H / 125°K T° class (H/163°C), standby 27°C H / 163°K AVR Regulation Yes Total Harmonic Distortion in no-load DHT (%) <2.5 Total Harmonic Distortion, on linear load DHT (%) <2.5 Wave form : NEMA=TIF <50 Wave form : CEI=FHT <2 Number of bearing Single Bearing Coupling Direct Voltage regulation at established rating (+/- %) 0,50 Recovery time (Delta U = 20% transcient) (ms) 500 Indication of protection IP 23 Technology Brushless | OTHER DATA Continuous Nominal Rating 40°C (kVA) 325 Standby Rating 27°C (kVA) 358 Efficiencies 100% of load (%) 94,10 Air flow (m3/s) 0,48 Short circuit ratio (Kcc) 0,4350 Direct axis synchro reactance unsaturated (Xd) (%) 316 Quadra axis synchro reactance unsaturated (Xq) (%) 161 Open circuit time constant (T'do) (ms) 2686 Direct axis transcient reactance saturated (X'd) (%) 11,70 Short circuit transcient time constant (T'd) (ms) 100 Direct axis subtranscient reactance saturated (X''d) (%) 9,40 Subtranscient time constant (T"d) (ms) 10 Quadra axis subtranscient reactance saturated (X"q) (%) 12,60 Subtranscient time constant (T"q) (ms) 10 Zero sequence reactance unsaturated (Xo) (%) 0,40 Negative sequence reactance saturated (X2) (%) 11,01 Armature time constant (Ta) (ms) 15 No load excitation current (io) (A) 0,81 Full load excitation current (ic) (A) 2,94 Full load excitation voltage (uc) (V) 42,80 Engine start (Delta U = 20% perm. or 30% trans.) (kVA) 788,58 Transcient dip (4/4 load) - PF : 0,8 AR (%) 13 No load losses (W) 4775,38 Heat rejection (W) 16270,88 Unbalanced load acceptance ratio (%) 100 |
| DIMENSIONS |
| DIMENSIONS AND NOISE LEVELS In compliance with 2000/14/CE standard Type soundproofing M228 Length (mm) 4475 Width (mm) 1410 Height (mm) 2430 Dry weight (kg) 4035 Tank capacity (L) 470 Acoustic pressure level @1m in dB(A) 50Hz (75% PRP) 77 Sound power level guaranteed (Lwa) 50Hz (75% PRP) 97 Acoustic pressure level @7m in dB(A) 50Hz (75% PRP) 67 Dimensions DW compact version Length (mm) 4527 Width (mm) 1400 Height (mm) 2068 Dry weight (kg) 3647 Tank capacity (L) 1368 | Dimensions soundproofed version Type soundproofing M228 Length (mm) 4475 Width (mm) 1410 Height (mm) 2430 Dry weight (kg) 4035 Tank capacity (L) 470 Acoustic pressure level @1m in dB(A) 50Hz (75% PRP) 81 Sound power level guaranteed (Lwa) 50Hz (75% PRP) Acoustic pressure level @7m in dB(A) 50Hz (75% PRP) 71 DIMENSIONS DW AND NOISE LEVELS In compliance with 2000/14/CE standard Type soundproofing M228 DW Length (mm) 4527 Width (mm) 1410 Height (mm) 2700 Dry weight (kg) 4588 Tank capacity (L) 1368 Acoustic pressure level @1m in dB(A) 50Hz (75% PRP) 76 Sound power level guaranteed (Lwa) 50Hz (75% PRP) 97 Acoustic pressure level @7m in dB(A) 50Hz (75% PRP) 67 |

| V350C2 CONTROL PANEL |
| --- |
| APM403, basic generating set and power plant control The APM403 is a versatile control unit which allows operation in manual or automatic mode Measurements : voltage and current kW/kWh/kVA power meters Standard specifications: Voltmeter, Frequency meter. Optional : Battery ammeter. J1939 CAN ECU engine control Alarms and faults: Oil pressure, Coolant temperature, Overspeed, Start-up failure, alternator min/max, Emergency stop button. Engine parameters: Fuel level, hour counter, battery voltage. Optional (standard at 24V): Oil pressure, water temperature. Event log/ Management of the last 300 genset events. Mains and genset protection Clock management USB connections, USB Host and PC, Communications : RS485 INTERFACE ModBUS protocol /SNMP Optional : Ethernet, GPRS, remote control, 3G, 4G, Websupervisor, SMS, E-mails | APM802 dedicated to power plant management The new APM802 command/control system is specifically designed for operating and monitoring power plants for markets including hospitals, data centres, banks, the oil and gas sector, industries, IPP, rental and mining. This unit is available as standard on all generating sets from 275 Kva designed for coupling. It is optional on the rest of our range. The Human Machine Interface, designed in collaboration with a company specialising in interface design, facilitates operations with a large 100% touch screen. The pre-configured system for power plant applications features a brand new customisation function which complies with the international standard IEC 61131-3. New communication functions (PLC and regulation), improve the high level of equipment availability in the installation. Advantages: Dedicated to power plant management. Specially researched ergonomics. High level of equipment availability. Modularity and long service life guaranteed. Making it easy to extend the installation For more information, please refer to the sales documentation. |

| M80, transfer of information The M80 is a dual-function control unit. It can be used as a basic terminal block for connecting a control box and as an instrument panel with a direct read facility, with displays giving a global view of your generating set's basic parameters. Offers the following functions: Engine parameters: tachometer, working hours counter, coolant temperature indicator, oil pressure indicator, emergency stop button, customer connection terminal block, CE. | Basic terminal block The control unit can be used as a basic terminal block for connecting a control box. Offers the following functions: emergency stop button, customer connection terminal block, CE. |
| --- | --- |